## Sheet1
Failure id | Asset type | Asset config id | Event description | Mode id | Date | Time | Detection | Service delay | Immediate investigation | Failure type | Safety failure | Hazard id | Cm description | Replaced asset config id | Cm start date | Cm start time | Cm end date | Cm end time | Oem failure reference | defect
1 | UPS | BRK-CC-UPS | One UPS found defective |  | 2024-02-06 | 10:00 |  | 0 | Immediate investigation carried out and defective UPS was replaced with spare UPS and defective UPS delivered to OEM premises for repairing | Hardware | No |  | Defective UPS was repaired at OEM premises and spare UPS has been replaced with repaired UPS. |  | 2024-02-06
2 | ACO | ALH-152-ACO | ACO card defective at ALH-152 |  | 2024-03-19 | 10:00 |  | 0 | Contractor jointly checked ACO panel at ALH-152 | Hardware | No |  | ACO's faulty card was replaced and ACO made functional in Auto mode.
3 | Steel Rope | DDR-KRJ-SS Rope | SS Rope 3 pully to counter weight, stain found broken at location 895/04 R |  | 2024-07-10 | 10:00 | Inspection | 0 | 4 strain found in broken condition at 894/04R | Hardware | No |  | Defective SS rope has been replaced with good condition SS rope under power and traffic block. |  | 2024-07-11 |  | 2024-07-11
4 | Traction Transformer | BRK-ASS-500kVA DT | Leakage in Distribution Transformer at Boraki Station |  | 2024-01-21 | 10:00 | Inspection | 0 | Standby transformer Jointly checking with DFCC and PMC | Hardware | No |  | Transformer's OEM was called to rectifiy the standby distribution transformer and OEM has rectified the leakage |  | 2024-02-23 |  | 2024-02-23
5 | 42kV LA | WIR-TSS-LA-01 | 25 kV LA burst at Wair TSS |  | 2024-03-06 | 10:00 | Failure | 720 | LA burst and nearby isolator flashed and connector got affected cause operation of isolator has affected and flash during open and close. | Hardware |  |  | LA has been replaced under power block and isolator connector was also replaced |  | 2024-03-07 |  | 2024-03-07
6 | 120 kV LA | WIR-TSS-HVLA 16 | LA was found in red zone |  | 2024-05-03 | 10:00 | Inspection | 0 | Needle found in Red zone so tested and found that resistance less than standard | Hardware |  |  | LA has been replaced under power block with new LA during testing found satisfactory |  | 2024-05-04 |  | 2024-05-04
7 | 42kV LA | SIK-SSP-LA-04 | 25 kV LA burst at Sikandarpur SSP |  | 2024-05-02 | 10:00 | Failure | 60 | LA burst at Sikadarpur SSP, line made through immediately. | Hardware |  |  | LA has been replaced under power block with new LA during testing found satisfactory |  | 2024-05-03 |  | 2024-05-03
9 | DPIM | WIR-TSS-DM-194 | Sparking of The busbar connector, named “Expansion Type Terminal Connector to Suit 50 Dia Al Tubular Busbar to Terminal Pad of 25 connected with DM-194 B |  | 2024-09-11 | 10:00 | Inspection | 0 | It was found that four nuts and bolts had burned out due to the sparking. The primary cause of the sparking was the looseness of the Expansion Type Terminal Connector due to lack of maintenance | Hardware |  |  | The busbar connecrtor was replaced by using new one. After replacing the Expansion Type Terminal Connector, the sparking ceased, and the burned connector was handed over to the DFCC team on the same day. |  | 2024-09-11 |  | 2024-09-11
10 | ACO | ALH-153-ACO | ACO card defective at ALH-153 |  | 2024-09-13 | 10:00 | Inspection | 0 | Contractor jointly checked ACO panel at ALH-153 | Hardware |  |  | The faulty card was replaced during the power block, and the ACO functioned satisfactorily after the replacement of new card. |  | 2024-09-14 |  | 2024-09-14
11 | CRP | WIR-TSS-CRP | The AC Fail indications were showing in the alarm annunciator windows of three CRPs in the Control Room at Wair TSS |  | 27-09-024 | 10:00 | Inspection | 0 | The AC Fail indications were showing in the alarm annunciator windows of three CRPs in the Control Room at Wair TSS. After acknowledging the annunciator, the indication continued to glow continuously | Hardware |  |  | After the OEM's site visit, they found that the AC converter card was faulty. After replacing the three faulty cards, the performance of the three alarm annunciators was satisfactory |  | 2024-09-27 |  | 2024-09-27
13 | 120 kV LA | WIR-TSS-HVLA-19 | The IR value of HVLA-19 was not up to the required value |  | 2024-08-21 | 10:00 | Inspection | 0 | During periodic maintenance with the IR team, it was found that the IR value of HVLA-19 was not up to the required standard. | Hardware |  |  | The faulty HVLA was replaced with a new one, and its performance was satisfactory |  | 2024-08-22 |  | 2024-09-24
14 | 120 kV LA | WIR-TSS-HVLA-21 | The IR value of HVLA-21 was not up to the required value |  | 2024-08-21 | 10:00 | Inspection | 0 | During periodic maintenance with the IR team, it was found that the IR value of HVLA-21 was not up to the required standard. | Hardware |  |  | The faulty HVLA was replaced with a new one, and its performance was satisfactory |  | 2024-08-22 |  | 2024-09-24
15 | 120 kV LA | WIR-TSS-HVLA-15 | The IR value of HVLA-15 was not up to the required value |  | 2024-08-21 | 10:00 | Inspection | 0 | During periodic maintenance with the IR team, it was found that the IR value of HVLA-15 was not up to the required standard. | Hardware |  |  | The faulty HVLA was replaced with a new one, and its performance was satisfactory |  | 2024-08-22 |  | 2024-09-30
24 | SCADA Workstation | SIK-SSP-BM 227 | BM 277 Local & Remote status not updating on SCADA OCC |  | 2024-08-27 | 10:00 | Inspection | 0 | Jointly checked and found that BM 277 Local & Remote status not updating on SCADA OCC | Software |  |  | The fault adressed by Contractor immediately and local & remote status was updating as per site condition. |  | 2024-08-27 |  | 2024-08-28
26 | AFL | WIR-TSS-AFL Wair TSS | Error indication on AFL |  | 2024-05-20 | 10:00 | Inspection | 0 | Jointly checked and found that an error signal is showing on AFL. | Hardware |  |  | The fault adressed by Contractor immediately |  | 2024-05-30 |  | 2024-06-08
27 | 25kV PT | WIR-TSS-LVPT-4 | Fuse of LVPT-4 not holding |  | 2024-05-06 | 10:00 | Inspection | 0 | Jointly checked and found the LVPT-4 fuse is defective. | Hardware |  |  | The fault adressed by Contractor immediately and its performance was satisfactory. |  | 2024-05-06 |  | 2024-05-06
28 | TCB | WIR-TSS-TCB-23 | TCB 23 not closing by OCC |  | 2024-04-05 | 10:00 | Inspection | 0 | Jonintly checked and found a core of interlockig Isolator was damaged and TCB-23 not closed by OCC. | Hardware |  |  | The fault adressed by Contractor immediately and its performance was satisfactory. |  | 2024-04-05 |  | 2024-05-07