## Sheet1
Failure id | Asset type | Asset config id | Event description | Mode id | Date | Time | Detection | Service delay | Immediate investigation | Failure type | Safety failure | Hazard id | Cm description | Replaced asset config id | Cm start date | Cm start time | Cm end date | Cm end time | Oem failure reference | defect
1 | UPS | UPS | One UPS found defective | MD_001 | 06/02/2024 | 08:40:00 | Inspection | 0 | Immediate investigation carried out and defective UPS was replaced with spare UPS and defective UPS delivered to OEM premises for repairing | Hardware | No |  | Defective UPS was repaired at OEM premises and spare UPS has been replaced with repaired UPS. |  | 06-02-2024 | 13:50 | 45328 | 14:30 |  | No
2 | Auto Transformer | AT-46 | Alarm of Transformer Oil Level Indication is showing very Low, Low and High at time |  | 19/02/2024 | 18:30:00 | Inspection | 0 | Water Entered in MOG and terminal block damaged due to moisture | Hardware | No |  | Checked the found the water filled in MOG. Remove the MOG and clean properly and refixed the properly with connection and tightness done properly. |  | 21-02-2024 | 14:15 | 45343 | 15:00 |  | Yes
3 | Distribution Transformer | 500KVA DTR | Leakage in transformer at boraki station |  | 23/02/2024 | 10:10:00 | Inspection | 0 | Jointly checking with DFCC and PMC | Hardware | No |  | Transformer OEM was called to rectify the standy distribution transformer and OEM has rectified the leakage. |  | 45346 | 14:00 | 45346 | 15:00 |  | No
4 | ACO | ACO | ACO card defective at ALH-152 |  | 09/03/2024 | 20:00:00 | Inspection | 0 | Contractor jointly checked ACO panel at ALH-152 | Hardware | No |  | ACO's faulty card was replaced and ACO made functional in Auto mode. |  | 45362 | 11:00 | 45362 | 11:20 | Yes | Yes
5 | CB | TCB-23 | TCB 23 not closing by OCC |  | 05/04/2024 | 10:10:00 | Inspection | 0 | Jointly checked and found a core of interlockig Isolator was damaged and TCB-23 not closed by OCC. | Hardware | No |  | The fault adressed by Contractor immediately and its performance was satisfactory. |  | 45387 | 11:00 | 45387 | 11:25 | No | No
6 | 132 kV side LA | HVLA 16 | LA was found in red zone |  | 20/04/2024 | 12:00:00 | Inspection | 0 | Needle found in Red zone so tested and found that resistance less than standard | Hardware | No |  | LA has been replaced under power block with new LA during testing found satisfactory | Yes | 45405 | 13:10 | 45405 | 14:15 |  | Yes
7 | 25kVA side LA | LA-04 | 25 kV LA burst at Sikandarpur SSP |  | 02/05/2024 | 10:00:00 | Failure | 0 | LA burst at Sikadarpur SSP, line made through immediately. | Hardware | No |  | LA has been replaced under power block with new LA during testing found satisfactory | Yes | 45415 | 15:15 | 45415 | 16:20 |  | Yes
8 | LVPT | LVPT-4 | Fuse of LVPT-4 not holding |  | 06/05/2024 | 12:00:00 | Inspection | 0 | Jointly checked and found the LVPT-4 fuse is defective. | Hardware | No |  | The fault adressed by Contractor immediately and its performance was satisfactory. | Yes | 45418 | 15:00 | 45418 | 15:40 | Yes | No
9 | AFL | AFL Wair TSS | Error indication on AFL |  | 20/05/2024 | 10:00:00 | Inspection | 0 | Jointly checked and found that an error signal is showing on AFL. | Hardware | No |  | The fault adressed by Contractor immediately | Yes | 45432 | 13:00 | 45432 | 13:45 | No | No
10 | ATD Rope (SS) | SS Rope | SS Rope 3 pully to counter weight, stain found broken at location 894/04 R |  | 04/07/2024 | 11:00:00 | Inspection | 0 | 4 strain found in broken condition at 894/04R | Hardware | No |  | Defective SS rope has been replaced with good condition SS rope under power and traffic block. |  | 45484 | 11:30 | 45484 | 12:30 |  | Yes
11 | CRP | CRP for PGCIL CKT-2 | Defective Sigma Light indication |  | 29/07/2024 | 08:30:00 | Inspection | 0 | Contractor jointly checked that the open and closed indications/Sigma Light of CB-192 are showing simultaneously. | Hardware | No |  | Contractor investigated the issue and solve on spot |  | 45502 | 15:00 | 45502 | 15:30 | Yes | Yes
12 | 25 KVA AT | AT-25KVA | AT output voltage not came at GSMR 03 UP Line Building |  | 20/08/2024 | 11:00:00 | Inspection | 0 | Isolate the AT and check the IR Value | Hardware | No |  | It was found AT winding is burnt. Immediently replaced the AT and charged . | Yes | 45546 | 09:30 | 45546 | 11:20 |  | Yes
13 | HVLA for 132KV Side | HVLA -15 | The IR value of HVLA 15 was not up to the required value |  | 21/08/2024 | 10:30:00 | Inspection | 0 | During periodic maintenance with IR team ,it was found that IR value of HVLA-15 was not up to the required standard. | Hardware | No |  | The faulty HVLA was repllaced with a new one ,and its performance was satiisfactory. |  | 45525 | 13:15 | 45525 | 13:45 |  | Yes
14 | HVLA for 132KV Side | HVLA-19 | The IR value of HVLA 19was not up to the required value |  | 21/08/2024 | 16:30:00 | Inspection | 0 | During periodic maintenance with IR team ,it was found that IR value of HVLA-19 was not up to the required standard. | Hardware | No |  | The faulty HVLA was repllaced with a new one ,and its performance was satiisfactory. | Yes | 45559 | 11:00 | 45559 | 12:00 | Yes | Yes
15 | HVLA for 132KV Side | HVLA -21 | The IR value of HVLA 21 was not up to the required value |  | 21/08/2024 | 16:31:00 | Inspection | 0 | During periodic maintenance with IR team ,it was found that IR value of HVLA-21 was not up to the required standard. | Hardware | No |  | The faulty HVLA was repllaced with a new one ,and its performance was satiisfactory. | Yes | 45559 | 10:00 | 45559 | 11:00 | Yes | Yes
16 | SCADA |  | Link of telecom with OCC was failed during inspection of GSM-R |  | 22/08/2024 | 11:30:00 | Inspection | 0 | Link fail occure at all GSMR | Software | no |  | The fault adressed by Contractor immediately |  | 45526 | 12:00 | 45526 | 12:20 | Yes | Yes
17 | SCADA | BM 227 | BM 277 Local & Remote status not updating on SCADA OCC |  | 27/08/2024 | 13:30:00 | Inspection | 0 | Jointly checked and found that BM 277 Local & Remote status not updating on SCADA OCC | Software | No |  | The fault adressed by Contractor immediately and local & remote status was updating as per site condition. |  | 45531 | 14:15 | 45531 | 14:30 | No | Yes
18 | Isolator DM-194B | DM-194 | Sparking of The busbar connector, named “Expansion Type Terminal Connector to Suit 50 Dia Al Tubular Busbar to Terminal Pad of 25 connected with DM-194 B |  | 07/09/2024 | 11:00:00 | Inspection | 0 | It was found that four nuts and bolts had burned out due to the sparking. The primary cause of the sparking was the looseness of the Expansion Type Terminal Connector due to lack of maintenance | Hardware | No |  | The busbar connector was replaced by using new one. After replacing the Expansion Type Terminal Connector, the sparking ceased, and the burned connector was handed over to the DFCC team on the same day. | Yes | 45542 | 13:30 | 45542 | 14:40 | Yes | No
19 | Traction Transformer 32 | TR-32 | Alarm of Transformer Oil Level Indication is showing very Low, Low and High at time |  | 10/09/2024 | 10:20:00 | Inspection | 0 | Water Entered in MOG and terminal block damaged due to moisture | Hardware & Software | No |  | After inspection water content remove from MOG, high alarm omitted but oil level low and very low alarms are still persisting. OEM neeed to visit |  | 45548 | 11:10 | 45548 | 12:00 |  | No
20 | ACO | ACO | ACO card defective at ALH-153 |  | 13/09/2024 | 12:30:00 | Inspection | 0 | Contractor jointly checked ACO panel at ALH-153 | Hardware | No |  | The faulty card was replaced during the power block, and the ACO functioned satisfactorily after the replacement of new card. |  | 45549 | 14:30 | 45549 | 14:45 |  | Yes
21 | 25kVA side LA | LA-05 | 25 kV LA burst at wair TSS |  | 21/09/2024 | 10:00:00 | Failure | 0 | LA burst and nearby isolator flashed and connector got affected cause opeartion of isolator has affected and flash during open and close | Hardware | No |  | LA has been replaced under power block and isolator connetor was also replaced | Yes | 45556 | 11:30 | 45556 | 12:00 |  | Yes
22 | 25kVA side LA | LA-06 | LA was found in red zone |  | 21/09/2024 | 10:00:00 | Inspection | 0 | Needle found in Red Zone so tested and found that resistance less than statdard | Hardware | No |  | LA has been replaced under power block with new LA during testing found satisfactory | Yes | 45556 | 12:00 | 45556 | 12:30 |  | Yes
23 | 25kVA side LA | LA-07 | LA was found in red zone |  | 21/09/2024 | 10:00:00 | Inspection | 0 | Needle found in Red Zone so tested and found that resistance less than statdard | Hardware | No |  | LA has been replaced under power block with new LA during testing found satisfactory | Yes | 45556 | 12:30 | 45556 | 13:00 |  | Yes
24 | 25kVA side LA | LA-08 | LA was found in red zone |  | 21/09/2024 | 10:00:00 | Inspection | 0 | Needle found in Red Zone so tested and found that resistance less than statdard | Hardware | No |  | LA has been replaced under power block with new LA during testing found satisfactory | Yes | 45556 | 13:00 | 45556 | 13:30 |  | Yes
25 | CRP | CRP | The AC Fail indications were showing in the alarm annunciator windows of three CRPs in the Control Room at Wair TSS |  | 27/09/2024 | 10:30:00 | Inspection | 0 | The AC Fail indications were showing in the alarm annunciator windows of three CRPs in the Control Room at Wair TSS. After acknowledging the annunciator, the indication continued to glow continuously | Hardware | No |  | After the OEM's site visit, they found that the AC converter card was faulty. After replacing the three faulty cards, the performance of the three alarm annunciators was satisfactory |  | 45562 | 16:40 | 45562 | 17:00 | Yes | Yes
26 | AT | AX-45 | Oil Leakage in transformer |  | 11/10/2024 | 13:40:00 | Inspection | 0 | Jointly checking with DFCC and PMC | Hardware | No |  | Transformer OEM was called to rectify and OEM has rectified the leakage. |  | 45576 | 15:45 | 45576 | 16:40 |  | Yes
27 | HVLA for 132KV Side- LILO CKT-01 | HVLA -12 | The IR value of HVLA 12 was not up to the required value |  | 14/01/2025 | 16:30:00 | Inspection | 0 | During periodic maintenance with IR team ,it was found that IR value of HVLA-12 was not up to the required standard. | Hardware | No |  | The faulty HVLA was repllaced with a new one ,and its performance was satiisfactory. | Yes | 45671 | 14:00 | 45671 | 15:30 |  | Yes
28 | HVLA for 132KV Side- LILO CKT-02 | HVLA -13 | The IR value of HVLA 13 was not up to the required value |  | 27/01/2025 | 12:31:00 | Inspection | 0 | During periodic maintenance with IR team ,it was found that IR value of HVLA-12 was not up to the required standard. | Hardware | No |  | The faulty HVLA was repllaced with a new one ,and its performance was satiisfactory. | Yes | 45684 | 13:00 | 45684 | 14:00 | Yes | Yes
29 | ATD Rope (SS) | SS Rope | SS Rope 3 pully to counter weight, stain found broken at location 853/19 R |  | 28/02/2025 | 13:00:00 | Inspection | 0 | 4 strain found in broken condition at 853/19R | Hardware | No |  | Defective SS rope has been replaced with good condition SS rope under power and traffic block. |  | 45716 | 14:00 | 45716 | 15:45 |  | Yes